## Slide 3: Hydraulic Profiles in Wastewater Treatment Plants
Source
Syed Qasim, 1999. Wastewater Treatment Plants: Planning, Design and Operation, 2nd Edition, Technomic, Lancaster, PA, 1106 p.

## Slide 4: Hydraulic Equations
Energy and Continuity Equations
Friction Head Losses – Hazen-Williams
Minor Head Losses
Open Channel Flow
  Uniform flow with Manning Equation
Weirs
  Appropriate weir equation, may have multiple

## Slide 31: Flows and Head Losses
Energy equation is used everywhere!
Bar rack
  Head losses
    Expansion
    Through bars
  Critical flow at effluent structure free overfall
  Proportional weir
Pump station
  System head curve – static lift, friction and minor losses
  Pump performance

## Slide 32: Flows and Head Losses
Venturi flow meter
  Venturi equation
Grit chamber
  Sized based on detention time and flow
  Overflow rate based on area
  Head losses in influent channel
  Weir flow for effluent flow
  Backwater analysis for flume with free overfall
  Head loss caused by drag forces on baffle walls

## Slide 33: Flows and Head Losses
Primary Sedimentation
  Sized for detention time and flow
  Overflow rate
  Head losses in influent structure, may include orifice flow through baffle wall
  Weir flow at effluent structure
  Open channel flow depth in launder
  Head loss in pipe after launder
  Junction box shows local total head

## Slide 34: Flows and Head Losses
Secondary Reactors
  Sized for detention time and flow
  Head losses in influent structure
  Weir flow at effluent structure
  Head loss in pipe to secondary clarifiers
Secondary Clarifiers – like primary sedimentation
  Head loss in pipe after launder
  Junction box shows local total head

## Slide 35: Flows and Head Losses
Disinfection
  Sized based on lamp operation
  Head loss through lamps
  Head loss through influent structure, typically rectangular weir
  Parshall flume – see manufacturer’s specifications for head loss and flow relationship
Outfall
  Open channel flow – Manning equation
  Outfall pipe – friction and minor losses